|  | TABLE OF CONTENTS |  | Page |
| --- | --- | --- | --- |
| 1.0 |  | SCOPE OF WORKS ............................................................................................................................. | 2 |
| 2.0 |  | GENERAL REQUIREMENTS ............................................................................................................ | 3 |
| 3.0 |  | SYSTEM REQUIREMENTS ............................................................................................................... | 4 |
| 4.0 |  | FUNCTIONAL REQUIREMENTS ..................................................................................................... | 5 |
|  | 4.1 | Calling condition ................................................................................................................................... | 5 |
|  | 4.2 | Fault warning condition ........................................................................................................................ | 5 |
|  | 4.3 | Fault monitoring .................................................................................................................................... | 6 |
| 5.0 |  | VISUAL INDICATORS REQUIREMENTS ....................................................................................... | 6 |
| 6.0 |  | SYSTEM DESCRIPTIONS .................................................................................................................. | 7 |
|  | 6.1 | System configuration ............................................................................................................................ | 7 |
|  | 6.2 | Main Fireman Telephone Panel (MFTP) .............................................................................................. 6.2.1 System Status Panel .................................................................................................................... 6.2.2 Master Handset Panel .................................................................................................................. 6.2.3 Telephone Status Panel ............................................................................................................... 6.2.4 Battery charger and power supply unit ....................................................................................... 6.2.5 24 volts DC battery set ................................................................................................................ | 7 7 7 8 8 8 |
|  | 6.3 | Digital sub-panel RTTU ........................................................................................................................ | 8 |
|  | 6.4 | Remote Fireman Telephone Station ...................................................................................................... | 8 |
| 7.0 |  | SYSTEM FEATURES .......................................................................................................................... | 9-10 |
| 8.0 |  | CABLE REQUIREMENTS .................................................................................................................. | 10 |
| 9.0 |  | TECHNICAL SPECIFICATIONS ....................................................................................................... | 11-14 |
| 10.0 |  | SCHEDULE OF PRICES ..................................................................................................................... | 15 |
| 11.0 |  | APPENDIX A - DEVIATION LISTS .................................................................................................. | 16 |
| 12.0 |  | APPENDIX B - BATTERY CAPACITY CALCULATION ............................................................... | 17 |
| 13.0 |  | APPENDIX C - SYSTEM SCHEMATIC DIAGRAM / CONFIGURATION .................................... | 18 |

MICROPROCESSOR-BASED MULTIPLEX FIREMAN TELEPHONE SYSTEM

| 1.0 |  | SCOPE OF WORKS | Compliance Yes/No |
| --- | --- | --- | --- |
|  | 1.1 | The scope of works call for the supply, install, test, commission, handing over in working order and 12 months defect liability maintenance of the complete Microprocessor-Based Multiplex Fireman Telephone System and all materials in accordance to the specifications and as shown on drawings. |  |
|  | 1.2 | The contractor shall provide all labour, materials, tools and equipments required to complete the fireman telephone system installation. All materials supplied shall be new, free from defects and of best quality of their respective kind. |  |
|  | 1.3 | On completion of the installation, the contractor shall be responsible for obtaining written approval from the Chief Inspector of Fire Services (CIFS) Malaysia and other relevant authorities having jurisdiction, stating that the completed installation is in proper working order. |  |
|  | 1.4 | The cost of all necessary approvals shall be deemed to be included in the contract price. It is also the responsibility of the contractor to enter and expedite all correspondence in connection with the approvals. |  |
|  | 1.5 | Any deviation(s) from the specifications descript hereinafter shall be filled in the deviation list as provided in Appendix A, stating reasons and alternative solution(s), if any. It is understood that any deviations from the specification may result in the disqualification of tender contract. |  |

| 2.0 |  | GENERAL REQUIREMENTS | Compliance Yes/No |
| --- | --- | --- | --- |
|  | 2.1 | The Fireman Telephone System shall consist of a Main Fireman Telephone Panel (MFTP), digital sub-panels RTTUs (Remote Telephone Terminal Unit), remote fireman telephone stations and all necessary audio and visual elements. |  |
|  | 2.2 | The Fireman Telephone System shall be microprocessor-based multiplex type with all the remote fireman telephone stations’ wiring pulled to the digital sub-panels RTTUs. |  |
|  | 2.3 | The Fireman Telephone System shall form as a two-way communication system. Conference calls or party lines of more than 5 remote fireman telephone stations shall be provided. Conference calls or party lines shall be defined as simultaneous communication between master handset and more than two (2) remote fireman telephone stations. |  |
|  | 2.4 | All locations of remote fireman telephone stations shown in the drawings are approximate. The contractor shall check the site locations shown on the accompanying drawings and shall adjust accordingly to suit site conditions. Superintending Officer or Consulting Engineer’s approval shall be obtained prior to readjustments or installations. |  |
|  | 2.5 | The contractor shall submit complete layout and wiring diagrams, fireman telephone system schematic diagram, LED facial display panel drawing and system console/cabinet layout to Superintending Officer or Consulting Engineer for approval at least two (2) weeks prior to commencement of works. |  |
|  | 2.6 | The system shall be designed to be self supervising to detect and to monitor any wire breakage, wire shorted, unauthorized removal of remote handset, to annunciate and to display visual signal at MFTP. |  |
|  | 2.7 | Self-contained storage batteries complete with charger shall be provided to enable the system to be operational during main power supply and essential power supply failure. During such condition, battery capacity provided shall be able to maintain system operational for at least 72 hours and 3 hours remote fireman telephone stations activation condition. |  |
|  | 2.8 | A battery calculation data sheet (refer to Appendix B) shall be submitted for approval. |  |
|  | 2.9 | The battery charger shall be designed and rated so that a battery discharged to its final voltage can be recharged to at least 80% of its rated capacity within 24 hours and to its rated capacity within another 48 hours. |  |
|  | 2.10 | The system shall operate on incoming 240 Volt AC, 50 Hz main power supply and connected to essential power supply. The incoming main shall then be stepped down to 24 Volt DC for complete usage and operational by the MFTP, digital sub-panels RTTUs and remote fireman telephone stations. |  |
|  | 2.11 | Location of the MFTP shall be in the fire/security control center as shown in the drawing and the exact position shall be determined at site. |  |
|  | 2.12 | Console/cabinet housing for the MFTP shall also allow space to house the standby battery set. |  |
|  | 2.13 | Construction of console/cabinet housing shall have a classification of at least IP 2X. |  |
|  | 2.14 | At least 10% spare zones shall be provided at the MFTP. |  |
|  | 2.15 | System operation shall be by means of a 4x4 keys alphanumeric keyboard and system operation manual shall be submitted for reference. |  |

| 3.0 |  | SYSTEM REQUIREMENTS The Fireman Telephone System shall consist of the followings :- | Compliance Yes/No |
| --- | --- | --- | --- |
|  | 3.1 | A MFTP and it shall be microprocessor-based and come complete with console/cabinet housing to be located at the fire/security control center. |  |
|  | 3.2 | Digital sub-panels RTTUs (Remote Telephone Terminal Units) located at strategic locations or within the control console/cabinet of MFTP. |  |
|  | 3.3 | Remote fireman telephone stations located at strategic locations such as escape staircases, escape routes, lobbies, etc. |  |
|  | 3.4 | Uninterrupted power supply system (batteries) dedicated for providing power to the system during mains power supply failure. |  |
|  | 3.5 | Battery charger mounted within the console/cabinet housing of the MFTP. |  |
|  | 3.6 | All necessary audio devices and visual indicators at or within the MFTP. |  |
|  | 3.7 | Interfacing facilities for Colour Graphic Computer and Mimic panel. |  |
|  | 3.8 | All the necessary cabling in conduits or trunking for interconnecting the whole system. |  |

| 4.0 |  | FUNCTIONAL REQUIREMENTS |  | Compliance Yes/No |
| --- | --- | --- | --- | --- |
|  | 4.1 | Calling condition - This shall be the interaction, two way communication, party lines or conference calls between the master handset and the Remote Fireman Telephone Handsets. |  |  |
|  |  | 4.1.1 | Under “AUTO” mode - From remote fireman telephone station to master handset. |  |
|  |  |  | Lifting of the Handset from its cradle shall cause an audible and flashing visual signal to be activated at the MFTP. By lifting the master handset at the MFTP shall automatically silence the audible alarm, flashing visual signal shall become steadily lighted and at the same time establishing two way communication without depressing any keys at the operator keyboard. |  |
|  |  | 4.1.2 | Under “AUTO” mode - From master handset to remote fireman telephone station. |  |
|  |  |  | Calling of the remote fireman telephone station shall be performed through the operator keyboard at the MFTP. By keying in the appropriate address/code of the remote fireman telephone station shall cause an audible and flashing signals at the remote fireman telephone station. The lifting of the Handset from the cradle shall then silence the audible alarm and the flashing signal shall illuminate steadily indicating the communication link with the master handset at MFTP has been established. |  |
|  |  | 4.1.3 | Under “MANUAL” mode - From remote fireman telephone station to master handset. |  |
|  |  |  | Lifting of the Handset from its cradle shall cause an audible and flashing visual signal to be activated at the MFTP. By lifting the master handset at the MFTP and keying in the appropriate address/code, through the operator keyboard, of the remote fireman telephone station that was calling shall silence the audible alarm, flashing visual signal shall become steadily lighted indicating two way communication has been established. |  |
|  |  | 4.1.4 | Under “MANUAL” mode - From master handset to remote fireman telephone station. |  |
|  |  |  | Calling of the remote fireman telephone station shall be performed through the operator keyboard at the MFTP. By keying in the appropriate address/code of the remote fireman telephone station shall cause an audible and flashing signals at the remote fireman telephone station. The lifting of the Handset from the cradle shall then silence the audible alarm and the flashing signal shall illuminate steadily indicating the communication link with the master handset at MFTP has been established. |  |
|  | 4.2 | Fault Warning condition - Fault warning shall result in the following :- |  | Compliance Yes/No |
|  |  | 4.2.1 | An audible warning from a sounder (usually a buzzer) situated within the MFTP. Such warning sounder shall be distinctive and of a different character from any remote fireman telephone station calling sounder. |  |
|  |  | 4.2.2 | The occurrence of a fault in a different zone, while the sounder is silenced, shall cause the sounder to sound again. |  |
|  |  | 4.2.3 | A visible indication on the MFTP. |  |
|  |  | 4.2.4 | In the event of multi-zone operation, a separate visible indication shall be provided for each fault warning zone for item 4.2.2. |  |
|  |  | 4.2.5 | The calling condition responses shall not be inhibited by any fault warning unless the fault itself prevents the giving of such responses. |  |
|  |  | 4.2.6 | Fault indications may be suppressed during a call condition, but in this case any faults remaining after the call condition has been reset shall cause the fault indication to be restored. |  |

|  | 4.3 | Fault Monitoring - The fault warning condition responses as specified in item 4.2 shall be given within 10 seconds of the occurrence of any one of the followings :- |  | Compliance Yes/No |
| --- | --- | --- | --- | --- |
|  |  | 4.3.1 | Short circuit or disconnection of the connection to any normal power supply associated with the giving of a calling, or other total loss of power from such a normal power supply. |  |
|  |  | 4.3.2 | Short circuit or disconnection of any standby power supply associated with the giving of a call. |  |
|  |  | 4.3.3 | Short circuit or disconnection of any battery charging equipment associated with the giving of a call. |  |
|  |  | 4.3.4 | Short circuit or disconnection of the leads/wires to one or more remote fireman telephone station. Such faults shall not disable others from calling or giving of a fault. |  |
|  |  | 4.3.5 | Removal of any handsets or disconnection from its power supply. |  |
|  |  | 4.3.6 | Cessation of any scanning or interrogation process between the MFTP and any sub-panel RTTU. |  |
|  |  | 4.3.7 | Rupture of any fuse such as to prevent calling or giving of a fault. |  |
| 5.0 |  | VISUAL INDICATORS REQUIREMENTS |  | Compliance Yes/No |
|  | 5.1 | Visual indicators at MFTP shall be L.E.D. (Light Emitting Diode) type and identified as follows :- |  |  |
|  |  | 5.1.1 | Indicators for calling condition shall be red. |  |
|  |  | 5.1.2 | Indicators for fault condition shall be yellow or amble. |  |
|  |  | 5.1.3 | Indicator for A.C. ON shall be green. |  |
|  |  | 5.1.4 | Indicator for D.C. ON shall be green. |  |
|  |  | 5.1.5 | Indicator for A.C. FAIL shall be red. |  |
|  |  | 5.1.6 | Indicator for CHARGER FAIL shall be red. |  |
|  |  | 5.1.7 | Indicator for BATTERY LOW shall be red. |  |
|  |  | 5.1.8 | Indicators for other functions shall not be green. |  |

| 6.0 |  | SYSTEM DESCRIPTIONS |  | Compliance Yes/No |
| --- | --- | --- | --- | --- |
|  | 6.1 | System configuration - A typical system schematic diagram of a Microprocessor-based Multiplex Fireman Telephone System shall be as shown in Appendix C. It shall consist of three (3) portions. |  |  |
|  |  | 6.1.1 | A Main Fireman Telephone Panel (MFTP). |  |
|  |  | 6.1.2 | Digital sub-panels RTTUs (Remote Telephone Terminal Units) |  |
|  |  | 6.1.2 | Remote fireman telephone stations. |  |
|  | 6.2 | Main Fireman Telephone Panel (MFTP) - This shall be the central controller. All information processing, monitoring of calls and faults shall be done here. The processed and monitored data shall then be converted to understandable audio and visual information. It shall consist of the following essential components : a) System Status Panel (SSP), b) Master Handset Panel (MHP), c) Telephone Status Panel (TSP), d) Battery charger and power supply unit, and e) 24 V DC battery set. |  |  |
|  |  | 6.2.1 | System Status Panel - This shall be the system trouble indicators and keyboard panel. It shall consist of audible device and visual indicators for trouble indication and operator keyboard for system operation. The trouble indicators are meant for early detection of faults within the system. This panel shall contain the following elements : a) LED indicators for - AC ON - DC ON - AC FAIL - CHARGER FAIL - BATTERY LOW - “AUTO” ON / “MANUAL” OFF - SYSTEM FAULT b) An audible warning device (usually a buzzer). c) A D.C. voltmeter. d) A 16x1 character LCD (Liquid Crystal Display) panel for displaying executed command. e) An operator keyboard for command entry consisting of : e-1) ‘0 - 9’ alphanumeric keys. e-2) ‘CALL’ key for calling of remote fireman telephone station. e-3) ‘CUT’ key for resetting two-way communication. e-4) ‘ACK’ key for silencing of audible alarm or acknowledging incoming faults. e-5) ‘LAMP TEST’ key for checking all LED functionality. e-6) ‘ENTER’ key for confirming executed command. e-7) ‘AUTO/MANUAL’ key for selection of system operation to be under AUTO or MANUAL mode. |  |
|  |  | 6.2.2 | Master Handset Panel - This shall be the main handset used to communicate with any of the remote fireman telephone station. It shall consist of a moulded red plastic handset, equipped with a coiled cord, a dynamic receiver and a condenser mic transmitter. |  |

|  |  | 6.2.3 | Telephone Status Panel - This shall form the whole part of remote fireman telephone stations zone LED display/indication panel. Each panel shall consist of a ‘window box’ meant for labeling of remote fireman telephone station zone location. It shall have a capacity to label up to 20 remote fireman telephone stations details. It shall consist of 2 rows of LEDs. The first row of LEDs shall be red in colour designating master handset ‘CALL’ remote fireman telephone station or vice-versa. The second row of LEDs shall be amber in colour designating wiring ‘FAULT’ of the remote fireman telephone station or the remote fireman telephone station itself. |  |
| --- | --- | --- | --- | --- |
|  |  | 6.2.4 | Battery charger and power supply unit - This shall form the source of power supply for the complete fireman telephone system. The battery charger shall be able to provide boost charge. Input voltage to the charger shall be 240 volts AC, 50 Hz. Output voltage from the charger shall be regulated to 27.5-28.5 volts DC depending on type of battery used. The power supply unit shall convert the incoming 27.5-28.5 volts DC to other voltages required by other components and modules within the system. The charger shall be capable of charging a discharged battery within 24 hours by normal charge method to a fully charged condition. It shall be protected against short circuit with automatic over-current shutdown. The charger shall be of linear, constant voltage charging type to prevent unnecessary damages or shortening the lifespan of battery. When the battery is fully charged, the charger shall automatically switch to float charging. |  |
|  |  | 6.2.5 | 24 volts DC battery set - This shall form as backup/standby power supply in case of 240 V main AC failure. It shall be sealed lead acid or nickel cadmium type of sufficient capacity to maintain system operational for at least 72 hours and permitting 3 hours two-way communication between the master handset and up to 5 remote fireman telephone stations in case of 240 V main AC failure. The battery set shall be mounted in the lower compartment of the console/cabinet housing and the charging equipment shall be installed above it and readily accessible. |  |
|  | 6.3 | Digital sub-panel RTTU - This shall be the data gathering panel. All the wire terminations of remote fireman telephone stations (input points) shall be done at the RTTU. Upon sensing a change of state of any of the input points, the RTTU shall transmit the data to the central controller (MFTP) for processing. The central controller shall then perform the necessary function accordingly. |  |  |
|  | 6.4 | Remote fireman telephone station - This shall form the remote phone stations located at strategic locations, such as escape staircases, lobbies, pump room, lift motor room, etc., within the building to enable fire fighters to use these phone stations to communicate with the master handset at MFTP during fire situation. It shall be built in a red metal housing with glass front panel with a breakglass and key operated door. A heavy duty red colour handset complete with electronics shall be provided with each remote fireman telephone station. The handset shall contain a dynamic receiver and a condenser mic transmitter. The electronics shall contain a volume compensation circuitry to ensure two way conversation/communication is loud and clear irregardless of the cable distance between the master handset and remote fireman telephone station. Each remote fireman telephone station shall trigger a cyclic audible alarm and flashing visual indication when called by the master handset. When the handset is lifted, the audible alarm shall be muted and the flashing light shall illuminate steadily indicating two way communication is established. |  |  |

| 7.0 |  | SYSTEM FEATURES |  | Compliance Yes/No |
| --- | --- | --- | --- | --- |
|  | 7.1 | The Microprocessor-based Multiplex Fireman Telephone System shall be designed with the following features :- |  |  |
|  |  | 7.1.1 | The MFTP shall be microprocessor-based multiplexing with data gathering panels (RTTUs) located at strategic locations. |  |
|  |  | 7.1.2 | A standard MFTP shall have a capacity to interface up to 1920 remote fireman telephone stations. |  |
|  |  | 7.1.3 | Each RTTU shall have a capacity to interface up to 10 remote fireman telephone stations. |  |
|  |  | 7.1.4 | For future expansion, the system shall be flexible by only the addition of extra modules without extensive modification to the existing installation. |  |
|  |  | 7.1.5 | The system shall provide an efficient and direct two way communication between fire fighters in the building in the event of fire situation. |  |
|  |  | 7.1.6 | The MFTP shall have the facility of conference call/party line communication from master handset to more than five remote fireman telephone station. |  |
|  |  | 7.1.7 | The MFTP shall supervise continuously the whole system functionality and to annunciate audible and visual signals in normal and malfunction situations. |  |
|  |  | 7.1.8 | The remote fireman telephone station shall be housed in a lockable red metal housing with glass front panel. |  |
|  |  | 7.1.9 | The system shall have the capability for volume compensation irregardless of wire length between the remote fireman telephone station and master handset. |  |
|  |  | 7.1.10 | Interconnection from each remote fireman telephone station to the MFTP shall be two wires and non-polarized. |  |
|  |  | 7.1.11 | Calling from master handset to remote fireman telephone station shall be by means of a simple keyboard operation. |  |
|  |  | 7.1.12 | Each telephone status panel (zone L.E.D. display panel) shall consist of 40 rows of L.E.D. i.e. it shall be able to accommodate up to 40 remote fireman telephone stations’ details. |  |
|  |  | 7.1.13 | Ringing or engaged tone shall be available both at the remote fireman telephone station and master handset to show status of calling. |  |
|  |  | 7.1.14 | By using 2 pair of data cable and 1 pair of speech cable interlinking between two MFTPs, one MFTP shall have the capability to communicate with the other MFTP and all their remote fireman telephone stations. |  |
|  |  | 7.1.15 | Auto connection shall be provided when remote fireman telephone station calls the master handset. |  |
|  |  | 7.1.16 | The MFTP shall have the facility to link to colour graphic computer. |  |
|  |  | 7.1.17 | Built in surge arrestors shall be provided in the system. |  |
|  |  | 7.1.18 | The system shall be able to supervise and monitor constantly open-circuit and short-circuit of wiring of all the remote fireman telephone stations, display their status visually and annunciate audibly. |  |
|  |  | 7.1.19 | Facility for automatic voice recording message shall be provided. |  |
|  |  | 7.1.20 | Facility for linking to P.A. (Public Address) system for paging shall be provided. |  |
|  |  | 7.1.21 | Facility to incorporate a real time clock shall be provided. |  |
|  |  | 7.1.22 | Facility for linking to multi-colour mimic shall be provided. |  |
|  |  | 7.1.23 | It shall have an isolating switch to simulate A.C. mains failure. |  |
|  |  | 7.1.24 | It shall have a built-in watch-dog circuit to supervise functionality of CPU. |  |
|  |  | 7.1.25 | It shall be able to monitor and supervise failure of A.C. mains, standby power supply, and battery charging conditions. |  |
| 8.0 |  | CABLE REQUIREMENTS |  | Compliance Yes/No |
|  | 8.1 | A typical system wiring diagram shall be as shown in Appendix C. |  |  |
|  | 8.2 | Looping cables from RTTU to RTTU and back to the MFTP shall be as follows :- |  |  |
|  |  | 8.2.1 | For indoor installation, - 2 x 7/0.85 mm (4 mm-sq.) PVC cables for RTTU power supply. - 2 x 3/0.29 mm (1.5 mm-sq.) PVC cables as speech line. - 2 pair (4 cores) twisted and screened cables (PVC/Screen/PVC) for data transmission. Minimum size : 7 / 0.3 mm (5.4 mm-sq. overall size). |  |
|  |  | 8.2.2 | For outdoor installation, - 2 x 7/0.85 mm (4 mm-sq.) armoured cables for RTTU power supply. - 2 x 3/0.29 mm (1.5 mm-sq.) armoured cables as speech line. - 2 pair (4 cores) twisted, armoured and screened cables for data transmission. Minimum size : 7 / 0.5 mm (0.5 mm-sq. per core). |  |
|  | 8.3 | Cables required from remote fireman telephone stations to the RTTU shall be as follows :- |  |  |
|  |  | 8.3.1 | For indoor installation, - 2 x 3/0.29 mm (1.5 mm-sq.) PVC cables per remote fireman telephone station and no polarity is required. |  |
|  |  | 8.3.2 | For outdoor installation, - 2 x 3/0.29 mm (1.5 mm-sq.) armoured cables per remote fireman telephone station and no polarity is required. |  |
|  | 8.4 | As a precaution, the cable size chosen for RTTU power supply shall be such that the voltage reaching the furthest RTTU shall not be less than 22 volts DC. |  |  |
|  | 8.5 | The cables for speech lines as per items 8.2.1 and 8.2.2 shall be replaced to the screened and twisted type if the overall distance between the RTTU and MFTP exceeded 300 metres. |  |  |

| 9.0 |  | TECHNICAL SPECIFICATIONS |  |
| --- | --- | --- | --- |
|  | 9.1 | MAIN FIREMAN TELEPHONE PANEL (MFTP) |  |
|  |  | Manufacturer | Micro-CTL Automation Sdn Bhd |
|  |  | Panel model | 800-SE |
|  |  | Material of enclosure | Mild Steel |
|  |  | Colour of enclosure | Signal Red |
|  |  | Thickness of enclosure | 1.6 mm |
|  |  | Finishing of enclosure | Epoxy powder coated paint |
|  | 9.2 | SYSTEM STATUS PANEL (Trouble Indicator / Keyboard Panel) |  |
|  |  | Manufacturer | Micro-CTL Automation Sdn Bhd |
|  |  | Panel model | M800P-CPU |
|  |  | Type | Microprocessor based |
|  |  | Model of microprocessor | NXP MC68HC05/08 |
|  |  | Memory | 8K Byte EPROM /2K Byte RAM |
|  |  | Number of I/O Port | 1 serial & 2 parallel |
|  |  | Type of operator interface | Keyboard with 16 keys 16 x 1 Alphanumeric LCD display |
|  |  | Type of trouble indications | LEDs for AC ON, AC FAIL, DC ON, Charger Fail, Battery Low and System Fault |
|  |  | Type of meter | Minipa voltmeter 0 - 30 V DC |
|  |  | Power Consumption | 22-32 V DC, 50 mA or 1.5W |
|  |  | Panel Construction | Perspex on aluminium |
|  |  | Panel colour | Light gray/light blue/black labeling |
|  |  | Panel Dimension | 400 x 90 x 30 mm |
|  |  | Operating Temperature | 0-50 degree C |
|  |  | Operating Humidity (non-Condensation) | 5% to 95% |

|  | 9.3 | TELEPHONE STATUS PANEL (LED Display Panel) |  |
| --- | --- | --- | --- |
|  |  | Manufacturer | Micro-CTL Automation Sdn Bhd |
|  |  | Panel Model | M800SE-DP |
|  |  | Capacity Per Panel | Maximum 40 zones |
|  |  | Type of indications | Call - Red LED Fault - Amber LED |
|  |  | Zone Card Construction | Zone card model - MCP-8ZRV Capacity per zone card - 10 zones Wiring card model - MCP-8RT LED card model - MCP-8ZT |
|  |  | Power Consumption ( 40 zones) | 22-32 V DC, 20 mA or 0.6W |
|  |  | Panel Construction | Perspex on aluminium (1.4 + 1.4 mm thick) |
|  |  | Panel Colour | Light gray/light blue/black labeling |
|  |  | Panel Dimension (HxWxD) | 400 x 90 x 30 mm |
|  |  | Operating Temperature | 0 - 50 degree C |
|  |  | Operating Humidity (non-condensation) | 5% to 95% |
|  | 9.4 | MASTER HANDSET PANEL |  |
|  |  | Manufacturer | Micro-CTL Automation Sdn Bhd |
|  |  | Panel Model | M8P-MH |
|  |  | Handset Material | High Impact Thermoplastic |
|  |  | Handset Colour | Red |
|  |  | Constant Rating | 24 V DC/1 Amp |
|  |  | Transmitter | Condenser Mica |
|  |  | Receiver | Dynamic |
|  |  | Impedance | 150 Ohms |
|  |  | Panel Construction | Prospect on aluminum (surface panel) Mild-steel (flush panel) |
|  |  | Panel Color | Light gray/light blue/black labeling |
|  |  | Panel Dimension (HxWxD) | 400 x 90 x 30 mm |
|  |  | Operating Temperature | 0 - 50 degree C |
|  |  | Operating Humidity (non-condensation) | 5% - 9% |

|  | 9.5 | BATTERY CHARGER |  |
| --- | --- | --- | --- |
|  |  | Manufacturer | Micro-CTL Automation Sdn Bhd |
|  |  | Model | M8-CHG (1.5) |
|  |  | Charger Type | Constant Voltage |
|  |  | Input Voltage | 240V AC / 50 Hz |
|  |  | Charger Voltage (output voltage) | 27.5 - 28.5 V DC 1.2A |
|  |  | Ripple & Noise | 100 mV (RMS) maximum |
|  |  | Operating Temperature | 0 - 50 degree C |
|  |  | Operating Humidity (non-condensation) | 5% - 95% |
|  | 9.6 | FIREMAN TELEPHONE REMOTE STATION |  |
|  |  | Manufacturer | Micro-CTL Automation Sdn Bhd |
|  |  | Model | M8-FTRS |
|  |  | Handset Material | High Impact Thermoplastic |
|  |  | Handset Colour | Red |
|  |  | Constant Rating | 24 V DC / 1 Amp |
|  |  | Transmitter | Condenser Mica |
|  |  | Receiver | Dynamic |
|  |  | Impedance | 150 Ohms |
|  |  | Operating Temperature | 0 - 50% degree C |
|  |  | Operating Humidity (non-Condensation) | 5% - 95% |
|  | 9.7 | FIREMAN TELEPHONE BACK BOX |  |
|  |  | Manufacturer | Micro-CTL Automation Sdn Bhd |
|  |  | Model | M8-TBB (Telephone Back Box) |
|  |  | Material | Mild Steel |
|  |  | Colour | Signal Red |
|  |  | Thickness | 1.2 mm |
|  |  | Finishing | Epoxy Powder Coated Paint |
|  |  | Box Dimension (HxWxD) | 356 x 172 x 80mm |
|  |  | Box Cover Dimension (HxWxD) | Surface mount (M8-BC-S) 364 x 178 mm Flush Mount (M8-BC-F) 380 x 195 mm |

|  | 9.8 | REMOTE TELEPHONE TERMINAL UNIT (RTTU) |  |
| --- | --- | --- | --- |
|  |  | Manufacturer | Micro-CTL Automation Sdn Bhd |
|  |  | Model | RTTU (Remote Telephone Terminal Unit) |
|  |  | Material | Mild steel |
|  |  | Thickness | 1.2 mm |
|  |  | Colour | Red |
|  |  | Finishing | Epoxy powder coated paint |
|  |  | Dimension (H x W x D) | 292mm x 216mm x 90mm |
|  |  | Zone card model | M800-RTTU-CPU |
|  |  | Capacity of zone card | 10 maximum |
|  |  | Wiring termination card model | M800-RTTU-TER |
|  |  | Power consumption | 20 mA 0r 0.6 W, 22 - 32 volts DC |
|  |  | Operating temperature | 0 - 50 degree C |
|  |  | Operating humidity (non-condensation) | 5% - 95% |

| 10.0 |  | SCHEDULE OF PRICES |  | QTY. | UNIT PRICE (RM.) | TOTAL (RM.) |
| --- | --- | --- | --- | --- | --- | --- |
|  | 10.1 | MAIN FIREMAN TELEPHONE PANEL (MFTP) |  |  |  |  |
|  |  | 10.1.1 | System Status Panel complete with operator keyboard, LCD (Liquid Crystal Display) panel, trouble indicators, battery charger, DC power supply unit and software. |  |  |  |
|  |  | 10.1.2 | Master Handset Panel complete with master handset and electronic circuit. |  |  |  |
|  |  | 10.1.3 | Telephone Status Panel complete with Telephone zone card and facial LED display panels. |  |  |  |
|  |  | 10.1.4 | Sealed Lead Acid Battery AH 24V DC. |  |  |  |
|  |  | 10.1.5 | Console/cabinet housing for items 10.1.1 to 10.1.4 |  |  |  |
|  | 10.2 |  | Remote Fireman Telephone Station c/w casing, remote handset and electronic circuit. |  |  |  |
|  | 10.3 |  | Digital sub-panels RTTUs (Remote Telephone Terminal Units) |  |  |  |
|  | 10.4 |  | Lump sum wiring, conduits and/or trunkings. |  |  |  |
|  | 10.5 |  | Lump sum installation work inclusive of testing and commissioning. |  |  |  |
|  | 10.6 |  | Optional items 1) 2) 3) |  |  |  |
|  |  |  |  |  | TOTAL |  |

| 11.0 | APPENDIX A - DEVIATION LISTS |
| --- | --- |
| Items deviated | Reason and alternative solution(s) |

| 12.0 | APPENDIX B - BATTERY CAPACITY CALCULATION |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | The following battery capacity calculation shall base on specification set for the Fireman Telephone System to be operational during main AC and essential power supply failure. Capacity of this 24 V DC standby battery set shall satisfy the following 2 conditions. a) 72 hours full system operational during main AC and essential power supply failure. b) 3 hours two-way communication. |  |  |  |  |
|  | Description | Quantity | Current (A) per unit | Standby hours (H) | Total battery capacity (AH) |
|  | System Status Panel (Trouble indicators / keyboard panel) | 1 | 0.025 | 72 | 1.8 |
|  | Per 40 zones of telephone zone card at Telephone Status Panel (LED display panel) | Z | 0.01 | 72 | Z x 0.72 |
|  | Remote Fireman Telephone Station calling | R | 0.02 | 3 | R x 0.06 |
|  | Digital sub-panel RTTU | T | 0.02 | 72 | T x 1.44 |

ASSUMPTIONS :

1) Total Remote Fireman Telephone Stations calling shall not be more than 8 zones at any one time. Therefore R = 8.

2) Effectiveness of battery set is only 80%.

Therefore, battery capacity required shall be calculated as follows :-

{ 1.8 + (Z x 0.72) + (R x 0.06) + (T x 1.44) } x 100/80 AH = { 1.8 + (Z x 0.72) + (8 x 0.06) + (T x 1.44) } x 1.25 AH

= { 1.8 + (Z x 0.72) + 0.48 + (T x 1.44) } x 1.25 AH

= { 2.28 + (Z x 0.72) + (T x 1.44) } x 1.25 AH

As an example, a 20-storey building with 55 Remote Fireman Telephone Stations.

55 Remote Fireman Telephone Stations will require 6 units of telephone zone cards and 6 units of RTTUs.

Therefore, battery capacity shall be

{ 2.28 + (6 x 0.72) + (6 x 1.44) } x 1.25 AH = 17.1 AH

13.0   APPENDIX C - SYSTEM SCHEMATIC DIAGRAM / CONFIGURATION.